## TECHNICAL BID
TENDER DETAILS (TECHNICAL BID) |  |  |  |  | YES | COMPLIED | QUOTED
1 | HAL'S GST REGISTRATION NO: | 21AAACH3641R1ZJ |  |  | NO | NOT COMPLIED | NOT QUOTED
2 | Tender No. | HBS/19CB-1003/1-48 Dated: 01-06-2020 |  |  |  | NOT APPLICABLE | INCLUSIVE
3 | Tender Due Date and Time | Date: 15-07-2020 Time: 15:00 Hrs. (03:00 PM) |  |  |  | BETTER | NOT APPLICABLE
4 | Tender Type | E-OPEN TWO BID SYSTEM
5 | Public Procurement (Preference to Make in India) | Public Procurement (Preference to Make in India), Order 2017 issued by Govt. of India is applicable for this tender. (Documents appended in Tender Documents) Bidder must comply and submit the following documents duly filled and submit along with their quotation-- 1. APPENDIX-A Public Procuement Policy Terms & Conditions- 2. (ENCLOSURE-I) CHECK LIST for Public Preference Policy 3. (ENCLOSURE-II) Calculation of Local Content (To be submitted along with Price bid only) (for Indian Vendors only) 4. (ENCLOSURE-III) Format for Affidavit of Self Certification regarding Local Content (for Indian Vendors only)
6 | Item Description | SUPPLY, INSTALLATION, COMMISSIONING, PROVE OUT AND TRAINING OF 250 KVA UPS AS PER SPECIFICATION.
7 | Quantity | 1 NO.
VENDOR DETAILS
1 | Vendor Name | M/s.
2 | Vendor Address
3 | GST ID No:(Mandatorly submit the GST Registration Certificate)
4 | PAN No. (Please upload copy compulsorily)
5 | Website | http://
6 | Email
7 | Phone No:
8 | Fax No:
9 | Contact Person with Designation
10 | Mobile No:
OFFER DETAILS
1 | Offer reference No.
2 | Offer date
3 | Model No.
4 | Make
5 | Currency
CONFIRMATION TO TECHNICAL SPECIFICATION
Please choose any of the options "Complied"/"Not Complied"/"Not Applicable"/"Better" from the drop down menu and enter your comments in the "Remarks" column.
TECHNICAL SPECIFICATION FOR 250 KVA UPS |  |  | COMPLIED / NOT COMPLIED / NOT APPLICABLE / BETTER | REMARKS
1 | SCOPE:
Supply, Installation, commissioning and prove out of one number of 250 KVA UPS with 100 minutes back up time and comprising of IGBT Base rectifier and inverter with latest technology of IGBT based True on-line with double conversion technology.
2 | APPLICATION:
The UPS will be used to provide un-interrupted power supply to Ion Nitriding Furnace of heat treatment and plating shop.
3 | STANDARDS:
The UPS and all associated equipment and components shall be manufactured in accordance with the following applicable standards:
IEC 62040-1-1 : General and Safety requirements.
IEC 62040-2: Uninterruptible Power System (UPS) category C2: EMC requirements
IEC 62040-3: Performance requirements and Test Method
4 | QUALIFYING CRITERIA AND CREDENTIALS:
The supplier should have supplied similar UPS to reputed customers (Preferable PSUs/ Govt Organizations/ MNCs). Clientele list of reputed customers and customer feedback report, to whom similar equipment has been supplied to be submitted along with quotation.
5 | DESCRIPTION OF THE SYSTEM:
The UPS system, operating in double-conversion mode, shall include the components: Rectifier/charger, Inverter, Battery, Static Bypass Switch, Manual Maintenance Switch, User & Communication Interface, Battery management system and necessary safety & protection device to ensure the continuity of Electric Power to the Load within the specified tolerances, without interruption upon failure of the normal AC supply for a maximum protection time for which the UPS is designed with installed battery backup.
6 | TECHNOLOGY:
IGBT Rectifier & IGBT Inverter, Microprocessor based, true online double conversion, online with Isolation Transformer (Internal/External) with Compact design. The UPS shall be a VFI type producing an output sinusoidal waveform that is independent of both input supply Frequency & Voltage and performance acceptable for critical load as per IEC 62040-3 Standard.
7 | MODE OF OPERATION:
a) Normal mode: During Normal operation mode the load is to be supplied by the UPS inverter and rectifier/charger has to convert the mains AC power supply to DC to feed the power to Inverter as well as simultaneously float charging the Battery system.
b) Emergency / Battery Mode: Upon failure of the normal AC source, the inverter shall continue to supply the load from battery power without interruption, within the limits imposed by the specified battery backup time.
c) Recharge Mode: When the normal AC source is restored, the rectifier shall again power the inverter, without interruption to the load and the charger will automatically recharges the battery.
d) Bypass mode: In the event of an overload or inverter shutdown, load shall instantaneously transfer the static bypass switch with available bypass AC source without interruption. The load shall return back to UPS inverter on clearance of fault without any disturbance in the supply of power at output.
e) UPS maintenance mode: For maintenance purposes, the UPS shall include a mechanical maintenance bypass system. The system shall be designed to isolate the UPS while continuing to supply power to the load from the bypass AC source.
f) Battery maintenance mode: For safe maintenance on the battery, the system shall include a circuit breaker to isolate the battery from the rectifier, the charger and the inverter. When the battery is isolated from the system, the UPS shall continue to supply the load without interruption
8 | INPUT SIDE PARAMETERS:
a) Input Voltage to UPS : 400 ±15% volts, 3 Phase AC supply
b) Input frequency: : 50 ±5% Hz
c) Input current Thd Harmonics : < 3 % on Full Load
d) Input side power factor : >0.98
9 | OUTPUT OF UPS:
a) Rated RMS output Voltage : 415 , 3 phase
b) Power rating :250 KVA
c) Load Power factor : 0.9 (Applicable for all design calculation)
d) Out put frequency : 50 Hz
e) Output frequency regulation : 0.2% in unsynchronized mode
f) Efficiency : >92%
g) THD Voltage at Output : For Linear Load ≤ 2% For Non-Linear Load ≤ 5.0%
h) Overload capacity : 125% for 10 Min, 150% for 1 Min
i) Voltage regulation : ≤ ±1% STATIC load condition ≤ ±5% for Step load variation
j) Permissible crest factor : 3:1
10 | CHARGER / BATTERY
a) Type/ Make of Battery bank: 2 Volt Sealed Maintenance Free (SMF) VRLA (Valve Regulated Lead Acid Battery) type battery with suitable capacity i.e Ampere hour (AH) to cater 100 minutes backup shall be provisioned along with the UPS. The battery rating shall be selected considering ageing factor, Design margin, K factor, Temperature correction factor etc. Detail Battery calculation sheet shall be enclosed with the offer. Make: Exide/ Amararaja / HBL along with Battery Rack inter- connecting cables, Protection cover etc are to be supplied along with the batteries.
b) Battery circuit breaker : Battery circuit breaker shall be provided to isolate the battery bank from charger and inverter for safe maintenance.
c) Battery Self test facility : UPS should have manual & automatic user-defined intervals self- test system for battery bank to update battery parameters and detect any abnormalities.
d) Charger : Temperature compensated floating voltage, charger/rectifier shall convert AC to regulated DC for input to the Inverter and for charging the Battery. The AC ripple voltage of the rectifier DC output shall not exceed 1% rms of the float voltage.
e) Battery Charge Current Limiting: The rectifier/charger shall include a circuit to limit the battery charging current.
f) Fuse Protection: Each AC phase shall be individually fused with Fast acting fuses so that loss of any semiconductor/IGBT shall not cause cascading failures.
g) Battery Backup Testing: The supplier shall perform Battery testing to show 100 minutes backup at full load condition with in safe discharge limit of battery (ECV) during PDI of UPS by HAL representative at supplier site.
11 | INVERTER
a) For increased performance, the UPS shall have latest technology IGBT based Inverter with switching at high frequency in order to minimize output voltage distortion.
b) Overload Capability: The inverter shall be able to sustain an overload up to 125% for 10 Min, 150% for 1 Min and then the load shall be transferred to the bypass source with the inverter get disconnected automatically from the Load.
c) Output Frequency: The output frequency of the inverter shall be maintained in a phase-lock condition with the frequency of Bypass source for as long as it is within ±2% of the nominal value.
d) Fault sensing: Fault sensing shall be provided to isolate a malfunctioning inverter from the critical load bus to prevent disturbance of the critical load voltage beyond the specified limits.
e) Battery protection: The inverter shall be provided with monitoring and control circuits to protect the battery system from damage due to excessive discharge. Shutdown of the inverter shall be initiated when the battery has reached the end of discharge (EOD) voltage
12 | MAINS STATIC SWITCH (MSS)
a) The UPS shall be provided with MSS static bypass circuit for isolation of the inverter and provide a path for power directly from an alternate AC (bypass) source in case of maintenance and also Inverter Overload. The UPS control shall constantly monitor the availability of the inverter bypass circuit to perform a transfer.
b) Manual Load Transfers: UPS shall have provision for manual load transfer between the inverter output and the alternate AC source and shall be initiated from the control panel.
c) Automatic Load Transfers: UPS shall have provision for automatic load transfer between the inverter output and the alternate AC source and shall be initiated if an overload or short circuit condition is sustained for a period in excess of the inverter output capability. Transfers caused by overloads shall initiate an automatic retransfer of the load back to the inverter only after the load has returned to a level within the rating of the inverter source.
d) Back feed Protection: The static bypass shall be provided with detection and control circuits, to be used in conjunction with external automatic switchgear, in order to disconnect the bypass line in the event of a short-circuit being detected in the solid-state devices that form the bypass static transfer switch.
13 | MSS MAINTENANCE BYPASS:
A fully rated bypass circuit shall be fitted in the MSS to provide an alternative path for power flow from the alternate AC supply to the critical load for the purpose of maintaining all the UPS modules while they are completely powered down.
14 | PROTECTION
The inverter shall be provided with monitoring and control circuits to protect from the following:-
a) Input : Input single Phasing, Input under/over voltage, Negative phase sequence on input and Bypass, RC surge suppressor.
b) Battery : Battery low/deep discharges, DC over voltage, battery current limit, charger current limit, Battery circuit breaker.
c) Output: Under/over voltage, overload, short circuit, Inv. Over temperature
d) Emergency Power off (EPO) : A push button should be provided for immediate total shutdown of power of UPS in an emergency Situation.
15 | DISPLAY AND CONTROLS
a) LCD DISPLAY: UPS must be provided with LCD Display to measure and for fault logging of the following: a) AC Input/output Voltage per Phase, (b) Load percentage (c) DC Voltage (e) Battery Percentage (f) Output Frequency. In addition to the LCD display the on line flow diagram should be on front panel to show the mimic and running status of UPS.
b) ALARMS : AC failure, DC failure, UPS failure, Load on bypass, Over/under temperature, Overload, Inverter failure, Overload shut down, Emergency shutdown, Maintenance by pass on, DC over voltage, Low battery, Battery circuit breaker open, Battery on load, Mains failure, Rectifier failed or off , inverter unsynchronized.
16 | EXPANDABLE & SCALABLE POWER RANGES:
The UPS should have provision for Paralleling up to 4 UPS units for increasing total power capacity
17 | ENVIRONMENTAL CONDITION:
a) Altitude : 1000 mtrs above MSL without derating
b) Humidity : 35 - 90% non conducive
c) Ambient temp. : 4 - 40ºC
d) Degree of Protection: UPS shall be prevented from falling dirt and dripping liquids from entering the UPS with IP-20 Degree of Protection.
GENERAL TERMS AND CONDITION
18 | Safety :
The equipment shall be provided with all safety features necessary to protect the equipment, controls and the operator while in operations from possible damage / injury. Noise level of the UPS, shall be less than 75 dB.
19 | Communication and Remote Assistance :
(a). The system should have provision for Remote monitoring through Ethernet TCP/IP or RS 485 over Modbus and SNMP (Single network monitoring program). Ups should have facility to communicate ups Converter/inverter electrical parameters measurements, Battery parameters and measurements to third party system via any of following communication protocol Mod bus /CAN bus,/Priofibus/Deviece net/TCP/IP.
(b). Suitable software shall be provided along with the equipment for remote monitoring of UPS.
20 | Installation and commissioning :
The supplier shall carry out installation and commissioning at HAL site within 30 days after site clearance report from HAL, Koraput.
21 | Spares:
a) General Spare parts for two years trouble free maintenance of the equipment shall be quoted separately (HAL reserves the right to procure).
b) Supplier shall ensure availability of spares for minimum 10 years (Desirable).
22 | After Sales Services:
After sales service by trained engineers should be provided during warranty period.
Quotation for AMC should be indicated separately in Price Bid (HAL reserves the right for selecting AMC at the time of placement of order.)
23 | Training:
The supplier has to provide free training to our engineers in the following areas for a period of 2 days at HAL site during commissioning in the following areas;
a) Operation
b) Mechanical Maintenance.
c) Electrical/Electronic Maintenance.
24 | Documentation / Certification:
UPS should be CE certified and certificate to be enclosed with the tender.
Test Certificate of the UPS & Batteries and WARRANTY certificates of the Batteries are to be supplied along with the equipment.
Three set of operation and Maintenance manual in English in Hard copy and Soft copy should be supplied along with the equipment.
25 | Pre-dispatch inspection (PDI):
The equipment should be offered for pre-dispatch inspection before final supply of the equipment. PDI will be carried out at supplier’s site by personnel from HAL.
Note: HAL reserves the right to waive off the pre-dispatch Inspection.
26 | Special Note:
a) The supplier should furnish the quantitative values with respect to specified values in the technical specification of the quote clearly, instead of mentioning “Complied”, “Agreed” or “Confirmed” etc. otherwise the tender quote is liable to be rejected.
b) Points other than Desirable are essential in nature.
c) Offers not meeting essential requirements shall not be considered.
PLEASE NOTE THAT THIS IS PART OF TECHNICAL BID. DONOT ENTER ANY PRICE, OTHERWISE YOUR OFFER WILL BE SUMMARILY REJECTED. JUST SPECIFY HERE WHETHER YOU HAVE QUOTED FOR THE CORRESPONDING ITEM IN THE PRICE BID OR NOT. |  |  |  | Quoted / Not Quoted / Inclusive / Not Applicable
1 | HSN Code of the item
2 | Basic Unit Price of the Item / Equipment
3 | Spares for 2 years trouble free operation (If quoted, provide Complete Breakup of each item WITHOUT price details in separate excel sheet)
4 | Spares for 10 years (If quoted, provide Complete Breakup of each item WITHOUT price details in separate excel sheet)
5 | After sales, service support with AMC (If quoted, provide Complete Breakup of each item WITHOUT price details in separate excel sheet)
6 | Packing & Forwarding Charges
7 | Ocean Freight & Marine Insurance
8 | Customs Duty
9 | Inland Freight & Insurance
10 | CGST % (FOR INDIAN VENDORS)
SGST % (FOR INDIAN VENDORS)
IGST % (FOR INDIAN VENDORS)
11 | Installation , Commissioning, Prove out & Training Charges
12 | GST on Installation, Commissioning, Prove out & Training
NOTE:
1 | All technical clarification regarding specification should be obtained before submitting the offer. Upon submission of offer, it is assumed that you have clearly & fully understood our requirement.
2 | Please note that no change in the price bid is possible and there is no provision of submitting additional prices of optional items after opening of technical bid in e-procurement system.
3 | Please ensure utmost care and caution while entering the data in the Price Bid. No typographical errors will be entertained afterwards.
4 | All the prices of all relevant items with complete price breakup should be furnished in the single Excel file only. Separate Excel Sheet in the same file may be used to furnish Price Breakup or other detailed information.
5 | In case of Two bid system, Prices should be entered only in the "Price Bid" Excel File. No Price details should be entered in any other uploaded document or Technical Bid. If prices are entered in the Technical Bid or any other document other than "Price Bid" Excel File, then your offer will be commercially rejected for violation of Two-bid system procedure.
6 | In case of any additional information, catalogues, brochures, please upload separate documents.
7 | In case of any queries, please contact us at +91-6853-221086. Fax no: +91-6853-222292/220401. Email is 'rabi.narayan@hal-india.com/ coml.koraput@hal-india.co.in'
8 | In case of any assistance required in downloading / uploading tender documents, please contact our helpdesk at +91-80-2566 7000/7001

## SPARES FOR 2 YRS
SPARES FOR TWO YEARS
Sl.No. | Item Description | HSN Code NO. | Item Code No. | Make | Quantity

## SPARES FOR 10 YRS
SPARES FOR TEN YEARS
Sl.No. | Item Description | HSN Code NO. | Item Code No. | Make | Quantity

## AFTER SALES AND SERVICE
AFTER SALES AND SERVICE WITH AMC
Sl.No. | Item Description | HSN Code NO. | Item Code No. | Make | Quantity